## Overview - BMSBAS
Building Management System - Overview.
Building Automation System (Building Management System).
Reference: | General Information about BMS: | https://en.wikipedia.org/wiki/Building_management_system
https://www.designingbuildings.co.uk/wiki/Building_management_systems_BMS
| "Competitor" / Peer reference | https://www.beckhoff.com/english.asp?applicat/building.htm?id=70997827099822?pk_campaign=AdWords-AdWordsSearch-BuildingAutomation_EN&pk_kwd=building%20management%20system
https://www.bsiddc.com/?gclid=Cj0KCQjw17n1BRDEARIsAFDHFeyCppOUGmNjG-NIwDLE1GdvGUfxvk3d78NTxzHXdC2I6tVkH6WpIcYaAuUtEALw_wcB
Systems: | Lighting | A way of providing advanced lighting options including multiple methods of controlling states of various lighting systems.
| Door Access | A way of securing and auditing room access by person and event.
| Information System | A display showing time, internal and external temperature and studio LIVE state, Managers Messages.
We may also add control of:
| Environmental | Ventilation.
Heating / Cooling.
Feedback from: | Security Alarm
Fire Alarm
Google Devices.
System type | This will be a proprietory design - so not compatible with C-Bus, Profibus, etc.
Triggers and relay control will function using discrete logic signalling instead of data will reduce building interference. A "Slow Bus" if you will...
Logic voltage : 5v DC.
Microcontrollers / embedded systems will communicate using ethernet.
Backup / replacement
A stock of drop in replacement modules for microcontrollers, relays and ethernet will be kept.
Firmware for all devices will be backed up to cloud, local servers and stored in a stock of SD cards where appropriate.

## Electrical Systems
Building Management System - Power Systems & Control.
Studio 3.0 - Electrical Systems: | LIGHTING SYSTEMS | [24 empty] | Mains Electrical Sockets | [7 empty] | Room Services | [7 empty] | Security |  | CCTV (Ethernet) |  | RFID Door Access System (Ethernet) |  | Data : Ethernet Networking
|  |  | PRIMARY LIGHTING CIRCUITS | [7 empty] | ATMOSPHERIC LIGHTING CIRCUITS | [11 empty] | External System Trigger State | [25 empty] | 112
Totals: | 3 | 8 | 119 |  | 970 | 7.08 | 21.24 | Circuits: | 21 |  | 25 |  | 14 |  | Total Circuits: | 60 | [25 empty] | 26 |  | 27 |  | 16
[6 empty] | 0.06 | [19 empty] | 161 | Wall Locations: NOTE : L/R always from perspective looking front to back for North / South. Back to Front for East. Front to Back for West.
| Emergency | Exit | Primary Lights | Watts | Total Watts | Amps | Peak Surge | Detail | C# | Circuits | Atmospheric Lights | Detail | C# | Circuits | Room Switch | Location | Door RFID (Entrance ONLY) | Location | Ceiling Sensor | Action | Smart Control | Admin Interface | Fire Alarm | Security Alarm | Door RFID | Double Sockets | North (Towards Rear) | East | South (Towards Front) | West | Purpose | Assumed Power Consumption | Circuit Detail: | Studio LIVE System | Detail |  | Detail | Circuits | Services | Detail | Circuits | Sensor | Details | Cameras | Details | Door | Details | LAN ID | Double Sockets | North (Towards Rear) | East | South (Towards Front) | West | Purpose
Reception | 1 | 1 | 3 | 10 | 30 | 0.18 | 0.54 | 10w LEDs | 2 | [5 empty] | DOUBLE: 1. Recep 2. All Corridor) | Reception by Fire Panel. | ON | Entrance | 2 |  | Reception | Reception | ON | ON | ON | 5 | 1: Left (Sofa), 2: Right | 3: Middle, 4: Right | 5: Right of Door under window. | - | 3: TV. 4: Arcade | Low power - Computers, TVs. Most un-populated. One high power room heater (electric to max 3Kwh) | 1,2,3,4 : (CIRCUIT 01 PUBLIC OFFICES) fed from Hot Office 2. | 1 | Sign : Opposite entrance. | Google Doorbell | 12 - 18v AC. |  |  |  |  | 2 | 1: Door. 2: NE - PIR. | 2 | 1. NE Corner facing Door. 2: W Facing E | 1 |  | A
Corridor Recept | 0 | 3 | 10 | 10 | 100 | 0.6 | 1.8 | 10w LEDs | 2 | 1: 2 lights, Low Power (no activity after timeout) 2: Remaining Lights (Initial trigger to timeout after no activity, / triggered on Activity detected) | [5 empty] | (recep) |  |  | 1 |  |  |  | ON | ON | ON | 4 | - | 1. Centre between Meeting room and Hot Office Door. 2. Between hot office doors. | 3. Under Window | 4. Centre Managers office to Archive. | All for cleaners or temporary use. 3. Christmas Tree / Seasonal. | Higher power than average for short irregular bursts - Vacuum Cleaner. | 1,2 : (CIRCUIT 01 PUBLIC OFFICES) fed from Hot Office 1. 3,4: (CIRCUIT xx - Central Offices) from Managers Office | 2 | Sign : End of Corridor by Window. 2. Studio Perimeter. | [6 empty] | 2 | 1: S to N. 2: N to S. | 2 | 1. NW looking S. 2: SW Looking N.
Corridor Centre | 0 | 2 | 6 | 10 | 60 | 0.36 | 1.08 | 10w LEDs | 2 | 1: 2 lights, Low Power (no activity after timeout) 2: Remaining Lights (Initial trigger to timeout after no activity, / triggered on Activity detected) | [5 empty] | (recep) |  |  | 1 |  |  |  | ON | ON | ON | 1 | - | - | 1. Centre of corridor | - | All for cleaners or temporary use. | Higher power than average for short irregular bursts - Vacuum Cleaner. | 1: (CIRCUIT 02 COMPANY OFFICES) from Company Archive. | 1 | Sign : Along Wall | [6 empty] | 2 | 1: E looking W. 2: W looking E. | 2 | 1: E looking W. 2: W looking E.
Corridor Emergency Exit | 1 | 1 | 5 | 10 | 50 | 0.3 | 0.9 | 10w LEDs | 2 | 1: 2 lights, Low Power (no activity after timeout) 2: Remaining Lights (Initial trigger to timeout after no activity, / triggered on Activity detected) | [5 empty] | (recep) | ON | Emergency Exit / Loading | 2 |  |  |  | ON | ON | ON | 1 | - | - | - | 1. Right of Kitchen Door. | All for cleaners or temporary use. | Higher power than average for short irregular bursts - Vacuum Cleaner. | 1: (CIRCUIT 03 WATER ROOMS) from Kitchen. | 1 | Sign : In front of studio | [6 empty] | 2 | 1: N looking S. 2: S looking N. | 2 | 1: N looking S. 2: S looking N. | 1
Managers Office | 0 | 0 | 9 | 5 | 45 | 0.54 | 1.62 | GU10 LEDs | 3 | 4 Corner, Not Desk, Desk | 1 | Perimeter RGB LED | 1 |  | QUAD: 1. Corner, 2. Not Desk, 3. Desk, 4. RGB LED Strip | Inside room, by door, non-hinged side. | ON - All |  | 1 |  |  |  | ON | ON | ON | 7 | 1: Left Locker support. | 2: Left of wall. 3: Left Third. 4: Right of wall. 7: Floor Socket? Centre to Desk. | 5: Middle | 6: Left of wall centre to door. | 7. Computers. Others Laptops / General low volume use. | Low power - Computers, TVs. Most un-populated. One high power room heater (electric to max 3Kwh) | ALL: (CIRCUIT 02 COMPANY OFFICES) | 1 | Illuminator : Centre Wall to Managers Office. | [6 empty] | 1 | 1: NE looking SW. | - |  | 1 |  |  | 10
Directors Office | 0 | 0 | 9 | 5 | 45 | 0.54 | 1.62 | GU10 LEDs | 2 | 4 Corner, Others | 1 | Perimeter RGB LED |  |  | TRIPLE: 1. Corner, 2. Others, 3. Perimeter RGB LED Strip. | Inside room, by door, non-hinged side. | ON - Perimeter | [5 empty] | ON | ON | ON | 8 | 1: Left. 2: Right. | 3: Right of door (Non Hinge side). 4: Right. | 5: Left. 6: Middle. 7: Right. | 8: Middle. 9: Right. | Computers and General Use. 3: Cleaners. | Low power - Computers, TVs. Most un-populated. One high power room heater (electric to max 3Kwh) | ALL: (CIRCUIT 02 COMPANY OFFICES) | 1 | Illuminator : Centre Wall to Directors Office. | Sky / Satellite | Satellite dish |  |  |  |  | 1 | 1: NW looking SE. | - |  | 1 |  |  | 8
Company Archive | 0 | 0 | 2 | 30 | 60 | 0.12 | 0.36 | Batton LED | 1 | [5 empty] | SINGLE | External, by door, non-hinged side. | ON | [5 empty] | ON | ON | ON | 2 | - | 1: Left of door. | - | 2: Middle | Normally unused. All for cleaners or temporary use. | Generally unused. | ALL: (CIRCUIT 02 COMPANY OFFICES) | [8 empty] | 1 | 1: W looking E. | 1 | 1: W looking E. | 1 |  |  | 2
Cleaners Cupboard (Service) | 0 | 0 | 1 | 30 | 30 | 0.06 | 0.18 | Batton LED | 1 | [5 empty] | SINGLE | External, by door, non-hinged side. | ON | [5 empty] | ON | ON | ON | 2 | - | 1: Middle. | - | 2: Right. | Small Domestic Appliance charging. | Low Power - battery charging. | ALL: (CIRCUIT 02 COMPANY OFFICES) | [8 empty] | 1 | 1: S looking N. | 1 | 1: S looking N. | 1 |  |  | 2
Meeting Room | 0 | 0 | 10 | 5 | 50 | 0.6 | 1.8 | GU10 LEDs | 3 | Screen Corners, Edge, Desk. | 4 | Perimeter RGB LED & 3 Warehouse Mods | 2 | LED, Warehouse Mods. | 5: 1. Screen, 2. Edge, 3. Desk, 4. Perimeter LED, 5. Warehouse Mods. | Inside room, by door, non-hinged side. | ON - All | [5 empty] | ON | ON | ON | 10 | 1: Left. 2: Middle. 3: Right. | 4. Left. 5. Centre. 6: Right. | 7: Left. 8. Middle. 9: Right. | 10: Middle. | 5. Presentation TV | Low power - Computers, TVs. Most un-populated. One high power room heater (electric to max 3Kwh) | (CIRCUIT 01 PUBLIC OFFICES) | 1 | Sign : Back wall to corridor | Sky / Satellite | Satellite dish |  |  |  |  | 1 | 1: NE looking SW. | 1 | 1: NE looking SW. | 1 |  |  | 12
Hot Office 1 | 0 | 0 | 8 | 5 | 40 | 0.48 | 1.44 | GU10 LEDs | 2 | 4 Corner, Others | 4 | Warehouse Mods | 4 | Desk 1, Desk 2, Desk 3, Desk 4 | DOUBLE: 1. Corners, 2. Others. QUAD: 1. Warehouse Mod A, 2. B, 3. C, 4. D. | Inside room, by door, non-hinged side. | ON - 4 Corners, Others. | [5 empty] | ON | ON | ON | 22 | 1:2:: Left . 3: Middle. 4:5: Right. Upper Dedo Trunking 4:5:Left. 5: Centre. 6:7: Right. | 6:7 Desk 3. 8:9 Desk 6. 10:11: Desk 7. | 12:13: Left. 14 Middle. 15:16: Right. | 17: Left of South Door. 18: 19: Right of South Door. 20: 21: Left of North Door. 22: Right of North Door. | Computers, Laptops, Light post-production equipment. | Medium Power - Assume 4 (average) computers or laptops. One high power room heater (electric to max 3Kwh) | (CIRCUIT 01 PUBLIC OFFICES) | 1 | Sign : Upper wall, by door, non hinged side. | [6 empty] | 1 | 1: NE looking SW. | 1 | 1: NE looking SW. | 1 |  |  | 10
Hot Office 2 | 0 | 0 | 8 | 5 | 40 | 0.48 | 1.44 | GU10 LEDs | 2 | 4 Corner, Others | 4 | Warehouse Mods | 4 | Desk 1, Desk 2, Desk 3, Desk 4 | DOUBLE: 1. Corners, 2. Others. QUAD: 1. Warehouse Mod A, 2. B, 3. C, 4. D. | Inside room, by door, non-hinged side. | ON - 4 Corners, Others. | [5 empty] | ON | ON | ON | [6 empty] | Medium Power - Assume 4 (average) computers or laptops. One high power room heater (electric to max 3Kwh) | (CIRCUIT 01 PUBLIC OFFICES) | 1 | Sign : Upper wall, by door, non hinged side. | [6 empty] | 1 | 1: SE looking NW | 1 | 1: SE looking NW | 1 |  |  | 10
Production Studio | 1 | 0 | 4 | 10 | 40 | 0.24 | 0.72 | "House Lights" : Warehouse LEDs | 1 | [5 empty] | SINGLE. & SINGLE Illuminated Switch : Studio LIVE. | Inside room, by door, Nearest Edit Room. | ON - House Lights. | [5 empty] | ON | ON | ON | 27 | 1: Left Low. 2: Centre. 3: High. 4: Mid Left Low, 5: Cent. 6: High. 7. Mid Right Low. 8: Centre. 9: High. 10 Right Low. 11: Centre. 12: High. | Commando Socket, Ceiling Left. 3 Phases presented in single sockets. | 13: Left Low.14: Centre. 15: High. 16: Mid Left Low, 17: Cent. 18: High. 19. Mid Right Low. 20: Centre. 21: High. 22 Right Low. 23: Centre. 24: High. | 25: Left. 26: Left Middle. 27: Left Right Middle. Local Consumer Unit for socket switching, Right of window. | Video and Photographuc Production Equipment. | High Power - Studio lighting and Camera equipment. Option to run large tungsten and powerful lighting 3kw or more. High power fans / heaters. | (CIRCUIT 04 PRODUCTION A) | 1 | Illuminator : Upper wall, over main doors, centre. | [6 empty] | 3 | 1: N looking S. 2: S looking N. 3: East Centre looking W | 3 | 1: N looking S. 2: S looking N. 3: Centre Wide looking down. | 1 | Double door magnet. |  | 8
Sound Room | 0 | 0 | 6 | 10 | 60 | 0.36 | 1.08 | GU10 LEDs | 2 | Front, Back | 1 | Warehouse Mods |  |  | TRIPLE: 1. Front, 2. Back, 3. Warehouse Mods. & SINGLE Illuminated Switch : Studio LIVE. | Inside room, by door, non-hinged side. | ON - All | [5 empty] | ON | ON | ON | 8 | 1: Left. 2: Middle | 3: Right of door. 4: Right. | 5: Left. 6: Middle. 7: Right. | 8: Middle | Sound Production Equipment | Medium Power - Mixing desk, audio power amplifier, assorted rackmount equipment. | (CIRCUIT 04 PRODUCTION B) | 1 | Illuminator : Over Gallery Window | [6 empty] | 1 | 1: W looking E. | - |  | 1 |  |  | 6
Post Production / LIVE Gallery | 0 | 0 | 6 | 5 | 30 | 0.36 | 1.08 | LED Spot | 1 |  | 3 | Perimeter RGB LED & 2x Warehouse Mods | 2 | Perimeter, Warehouse. | TRIPLE: 1. Perimeter RGB LED, 2. LED Spots, 3. Warehouse Mods. & SINGLE Illuminated Switch : Studio LIVE. | Inside room, by door, non-hinged side. | ON - E Perimeter | [5 empty] | ON | ON | ON | 19 | 1: Left. 2: Middle. 3: Right. | 4. Left. 5. Middle Left. 6: Middle Right (not behind door). 18: Centre Left, 19: Centre Mid Right. | 7: Right of Door, 8: Right. | 9: Left. 10: Mid Left. 11: Mid Right. 12: Right. MIDDLE (Above Desk): 13: 14: 15: 16: 17: Spread equally left to right. | Live Streaming, Editing etc. Dual PSUs. Laptops. | Medium Power - Computers, Servers, Laptop, Post Production Equipment (tape desks, ATEM, rackmount equipment, etc). | (CIRCUIT 04 PRODUCTION B) | 1 | Sign : Over Gallery Window | Sky / Satellite | Satellite dish |  |  |  |  | 1 | 1: NW Looking SE. | 1 | 1: NW Looking SE. | 1 |  |  | 22
Workshop | 0 | 0 | 3 | 10 | 30 | 0.18 | 0.54 | Warehouse LEDs | 1 | [5 empty] | SINGLE | Inside room, by door, non-hinged side. | ON | [5 empty] | ON | ON | ON | 17 | 1: Left. 2: Middle. 3: Right. 4:5:6:7: Mid left to right. | 8: Middle. 9:10:11: Centre Left to Right. | 12: Left. 13: Middle. 14: Right. 15:16:17: Centre left to right. | - | Equipment construction and Repair, and Set building. | High Power - Occasional use of drills, saws. Lighter use with Power tool battery chargers. | (CIRCUIT 05 BACK STAGE) | 1 | Illuminator : On Cable ladder containment. | [6 empty] | 1 | 1: E looking W. | - |  | 1 |  |  | 10
Storage | 0 | 1 | 4 | 10 | 40 | 0.24 | 0.72 | Warehouse LEDs | 1 | [5 empty] | SINGLE | Inside room, by door, non-hinged side. | ON | [5 empty] | ON | ON | ON | 10 | 1:2 Left Low. 3:4:5:6:7: Centre Left. 8:9:10: Right, Centre by MCB Panel. | - | - | - | Production Equipment Battery Charging. Cleaners. | Low/Medium Power - Production Equipment Battery Charging. | (CIRCUIT 05 BACK STAGE) | [8 empty] | 2 | 1: W looking E. 2: E looking W. | 3 | 1: S opposite door, looking N to door. 2: W looking E. 3: E looking W. | 1 |  |  | 4
Secure Storage | 0 | 0 | 2 | 10 | 20 | 0.12 | 0.36 | LED Panel | 1 | [5 empty] | SINGLE | Inside room, by door, non-hinged side. | ON | [5 empty] | ON | ON | ON | 15 | 1: Left. 2: Middle. 3: Right. | 4: Left of door. | 5: Middle. 6: Right. | *** 3 PHASE. (P1) 7:8:9: Centre Mid Left. (P2) 10:11:12: Centre Mid Middle. (P3) 13:14:15: Centre Mid Right. | Dual PSU Servers, UPS systems. | High Power - Constant draw from racks of servers. Possible feed for Air Conditioning. | (CIRCUIT 06 - SERVERS Phase 1) (CIRCUIT 07 SERVERS - Phase 2) (CIRCUIT 08 SERVERS - Phase 3) | [8 empty] | 2 | 1: SE Looking W. 2: E looking W. | 2 | 1: SE Looking W. 2: E looking W. | 1 |  |  | -
Dressing Room | 0 | 0 | 8 | 5 | 40 | 0.48 | 1.44 | LED Spot, 4 GU10 LEDs | 2 | 4 Corner, Others | 1 | Mirror Actor Bulbs, Mirror Lights | 1 |  | TRIPLE: 1. Corner, 2. Others, 3. Mirror Actor Bulbs. FUSED SPUR (Mirror). | Inside room, by door, non-hinged side. | ON - ALL | [5 empty] | ON | ON | ON |  | 2: Left. | 2: Right of door. | 3: Left. 4: Right. 5: Centre Left. 6: Centre Middle. 7: Centre Right. | 8: Right. | Hair Dryers, Lights. | High Power - Occasional use for hair dryers. | (CIRCUIT 03 WATER ROOMS) | 1 | Sign : Above Mirror | [8 empty] | - |  | 1 |  |  | 4
Kitchen | 0 | 0 | 8 | 10 | 80 | 0.48 | 1.44 | 10w LEDs | 1 |  | 1 | Cabinet Lighting | 1 |  | DOUBLE: 1. LED 10w, 2. Cabinet Lighting. | Inside room, by door, non-hinged side. | ON- ALL | [5 empty] | ON | ON | ON | [5 empty] | Heating water and cooking. | High Power - Regular intermittent use by Oven, toaster, kettle, hot water heaters. | (CIRCUIT 03 WATER ROOMS) | 1 | Sign : Above Door | [6 empty] | 1 | 1: NW Looking SE. | - |  |  |  |  | 4
Toilet 1 | 0 | 0 | 2 | 10 | 20 | 0.12 | 0.36 | 10w LEDs | 1 | [5 empty] | SINGLE | External, by door, non-hinged side. | - | [5 empty] | ON | ON | ON | 0 | - | - | - | - | Hand dryer. | High Power - Short occasional bursts. | (CIRCUIT 03 WATER ROOMS) |  | Contactor Control : Hand Dryer | Hand Dryer | Contactor Controlled | Fused Spur 2.5mm. Upto 13 Amp | [5 empty] | - |  |  |  |  | -
Toilet 2 | 0 | 0 | 4 | 10 | 40 | 0.24 | 0.72 | 10w LEDs | 1 | [5 empty] | SINGLE | External, by door, non-hinged side. | - | [5 empty] | ON | ON | ON | 0 | - | - | - | - | Hand dryer. Alarm. | High Power - Short occasional bursts. | (CIRCUIT 03 WATER ROOMS) |  | Contactor Control : Hand Dryer | Hand Dryer | Contactor Controlled | Fused Spur 2.5mm. Upto 13 Amp | Panic Alarm Pull Cord | Ext RED Light. Siren? | Fused Spur. Lighting Mains Power. |  |  | - |  |  |  |  | -
[5 empty] | 0 |  | 0
External | 0 | 0 | 1 | 20 | 20 |  | 0 | PIR Floodlight | 1 | Security Light | 5 | Small decorative, Signage. | 2 |  | TRIPLE : 1. Floodlight, 2. Atmospheric. 3. Sign Lighting. | Corridor, by Fire exit on Directors Office wall. | - |  | Ext Light Sensor | ON when dark |  | External | ON | ON | ON | 3 |  |  |  | 1: Left. 2: Middle. 3: Right. | Flood Lighting | Low average, Medium peak Power - External LED flood lighting. | (CIRCUIT 09 EXT MAINS), (CIRCUIT 10 EXT CAR CHARGING) |  |  | Car Chargers | 2 Phase High Power. | [6 empty] | 5 | 1: E looking W. 3: N looking S. 3: W looking E to road. 4: CU Entrance. 5: CU Fire Exit.
| * Assumed 0.7 power efficiency. Reference: https://www.thecalculatorsite.com/conversions/common/watts-amps.php | [15 empty] | * Actioned, unless already actioned that day unless all lights are off, then ignore. | [9 empty] | * It is preferable to reduce use of 4 way socket adapters. As such production spaces and some offices have an above average quantity of mains sockets. | [17 empty] | 4x Panel:
| Assuming 3x current load for power on. | [25 empty] | It is not anticipated that every socket would be used to maximum potential current draw. Average socket consumption is likely to be less than 3 amps. | [17 empty] | https://www.amazon.co.uk/s?k=cat6+ethernet+socket&page=2&qid=1588542915&ref=sr_pg_2
[27 empty] | Sockets may be populated but many not in a continuous power on state. | [17 empty] | https://www.amazon.co.uk/kenable-Plate-Sockets-Keystones-Jacks/dp/B003OSUVNQ/ref=sr_1_36?dchild=1&keywords=cat6+ethernet+socket&qid=1588545414&sr=8-36&swrs=097CC891192D6B8A461EDF16111FBB13
https://www.amazon.co.uk/Comms2Go-CAT6-Double-Port-Faceplate/dp/B07SNFY2YD/ref=sr_1_84?dchild=1&keywords=cat6%2Bethernet%2Bsocket&qid=1588545727&sr=8-84&swrs=097CC891192D6B8A461EDF16111FBB13&th=1
| If power efficiency is 5.0, Average AMPS on lighting circuit is 8.7 Amps (Peak 3x at 27 amps). | [25 empty] | However, the circuit should anticipate normal use, and may need to be split into multiple circuits? | [17 empty] | 5x Doubles
| No circuit exceeds 10 amp max at power on, event at 5 times average load. As such, contactors shouldn't be needed. | [43 empty] | https://www.amazon.co.uk/deleyCON-CAT-Universal-Network-Socket/dp/B018IKEB0I/ref=sr_1_14?dchild=1&keywords=cat6+ethernet+socket&qid=1588542915&sr=8-14
10x Doubles
https://www.amazon.co.uk/deleyCON-10x-Universal-Network-Socket/dp/B07WC11Q36/ref=sr_1_53_sspa?dchild=1&keywords=cat6+ethernet+socket&qid=1588545564&sr=8-53-spons&swrs=097CC891192D6B8A461EDF16111FBB13&psc=1&spLa=ZW5jcnlwdGVkUXVhbGlmaWVyPUExRExBSDA1T0tINFVaJmVuY3J5cHRlZElkPUExMDM3MjE4MzBYMjNTNjhFNFQ4VCZlbmNyeXB0ZWRBZElkPUEwNTIyOTU5MTM4MjlDVTQ0M05YTyZ3aWRnZXROYW1lPXNwX2J0ZiZhY3Rpb249Y2xpY2tSZWRpcmVjdCZkb05vdExvZ0NsaWNrPXRydWU=
Double Port
https://www.amazon.co.uk/signal-CS13673-Sockets-Double-Keystones/dp/B003OSRHNI/ref=sr_1_38?dchild=1&keywords=cat6+ethernet+socket&qid=1588545564&sr=8-38&swrs=097CC891192D6B8A461EDF16111FBB13

## Electrical System Specification
Building Management System - Lighting Control
Studio 3.0 - Electrical System Specifications | [6 empty] | ALARM
BMS - Building Management System - Lighting.
Summary
[BMS/BAS] is a microcontroller / software driven central lighting control system, known as Building Light Control (BMS) System
All switches with the exception of the "Last Man Out" switch are effectively "soft" switches
Other "switch" / sensor / triggers / Web Interfaces (Including wall room switches) are simply logic signals to the BMS.
Sensors include PIR / Movement Sensors. Triggers include various alarms, studio LIVE, smart "Google" control and RFID.
On microcontroller failure, FAIL-SAFE all lights ON.
Safety / Power Outage / Failure
BMS is designed to prioritise the safety of the building's occupants as primary concern.
As a gas suppy is not installed in or near the building, failure in ON mode is safe.
In event of a Power Failure, a UPS system will maintain power to the entire lighting system.
In event of a UPS failure (regardless of input supply status), Non-maintained Emergency Lighting will illuminate.
This configuration effectively provides a double emergency lighting provision across the building.
The following Methods turn ON or OFF all building lights
|  | Last Person Out Switch |  |  | Turns all lights OFF, Turns lights ON according to physical switch setting.
|  | Administration Interface |  |  | Reads state for display. ON or OFF as user commanded
|  | Administration Interface AUTO |  |  | Timer manual control
Each circuit is controlled by individual 5v relays, to a MAX PEAK Power consumption of 9 Amps per relay (at power on).
QUERY - Relays could be located in a central box or each room.
|  |  | If in a central box, 35 lighting cables need to run from central box. |  |  | CHECK NUMBER
|  |  | If in each room, 11 lighting cables needed to run to each room / block of rooms. |  |  | CHECK NUMBER
Raspberry PI Control
Logic Sensing
Logic sensing from physical Situ switches & Last Person Out Switches
Movement Sensor
Door RFID system
Google / If This Then That - Home Device triggering.
Last state change from ANY prioritises, except for Administrator Override
Administrator Interface Override Option for ALWAYS ON (only), ignoring status changes from other logic control inputs.
GPIO is limited in quantity. As such, we should use a GPIO expander to sense and control the required quantities.
Recommended on the forums: Laqiya 5pcs MCP23017-E/SP 16 I/O Expander.
Reporting
Report lighting state to the RFID Door Access System Database.
Logic Sensing
To protect the I/O interface and microcontroller systems:
All incoming triggers (switches, movement, RFID, etc) - ground a logic source to trigger a LED at the controller in an Opto-isolator
Also meaning that triggers only handle low voltage / current - including usual light switches.
Conventional light switches will be installed throughout the building to enable accessibility and use by everyone.
However, the system will ony read changes that oppose the current state. E.G. a light already OFF will ignore a switch request to turn the light off.
There is a small risk that the user may not understand why a switch change did not effect lighting change. However, it is assumed that the significant majority of users will try the light switch again, achieving their intended outcome.
The purpose of this design is to maintain the up/down logic state of physical light switchs, and avoidl
for instance a condition where a double light switch turns lights on and off in opposite directions.

## DoorAccess-Spec-Function
Concept Television Studios Limited
Building Management System - Door Access
FUNCTION SPECIFICATION
| 2020-04-26 | PME | Creation
| 2020-04-27 | PME | Added Failure Conditions
Purpose
To audit people in the building.
For fire protection
for revenue protection
to protect assets
audit facility hire
To increase Security
Deterrent due to perception of complex security system
Audit trail
Access Control
Restrict access to the main building and rooms or areas within the building.
SAFETY
Release all doors on fire alarm trigger
Option to release all doors on power loss.
Break Glass to Exit - Security / safety door compromise from INSIDE rooms only.
Audit
Log all attempts to enter or exit a room.
Log all incident triggers (e.g. fire alarm).
Log all primary power loss.
Features
Announcer Screen OR LED indicators
Access granted
Access Granted - Please be quiet, Recording in process.
Access Denied. Please Contact X for assistance.
FIRE - Please exit the building NOW and report to FIRE ASSEMBLY POINT.
Announcer Audio
Access Granted sound
Access denied sound
FIRE sound
Power Failure Sound
Sound level - High / Low / Disabled
Read sound level from Primary Database
Sound level also set by Studio LIVE Logic signal
Waveform audio playback OR Buzzer sequences.
Lighting / Environmental Control
Reception lights always on when the building is occupied.
Room lights turned on when access is granted to a room.
Double Tap for 'last person out' to lock room and turn lights out.
Lock Control
Tap entry
Double Tap exit
Timed lock control - 20 seconds?
Access Photographs
Cameras mounted in RFID panel
Every access request triggers photo, appended log of ID
Optional video record until motion has ended -identifying multiple extrances and exits.
Motion trigger without RFID trigger logged as query.
Out of hours text prompt for no RFID exit
If user did not exit using RFID, text them at closing time to ask if they are still in the building
If no reply WAIT 1 hour and repeat
If YES, append text exit reference to User ID log
If NO, append prompt response to User ID Log
RFID Tag Security
Non-Sequential ID numbering to prevent 'Guess'
Write last 10 access IDs (Including new) to RFID to prevent multi-presentation.
If tag duplicated, either original or duplicate will allow one further access, but the other will fall out of sequence.
User ID Management
ID Profile
Name
Photo
Address
Mobile Phone Number
Email Address
Any access permitted
Room access list permitted
Access Log - Date and Time entry and exit logs
Access Log - Access point photographs
Edit
Remove but retain logs
Remove and wipe (GDPR)
View And Control permitted access by Room
View list of rooms
View IDs allowed to each room (IDs clickable to full ID info
Remove access to ID
Display Panel
Who's in? (Including arrival time)
Time
Who left today (and at what time)
Local weather
Corridor Temperature
External Temperature
Failure Conditions and Solution
Main Database Server Down
Local RFID Access system stores last permission list and acts according to that requirement.
Send message to Administrator - "No access to Primary DB" - for example.
Power Failure
Facility Access System should be connected to the site UPS.
On total powerloss, door is opened.

## DoorAccess-Spec-Implementation
Concept Television Studios Limited
Building Management System - Door Access
IMPLEMENTATION SPECIFICATION
| 2020-04-27 | PME | Creation
Principle Requirements |  |  |  | Proposed Solution |  |  | Considerations
| Durable mounting for RFID System |  |  | 3d Print from custom design. Lid to standard / off-shelf back box?
| Primary Server - Database / Admin Interface |  |  | VM instance, Ubuntu, MYSQL. Fair storage for access photographs.
|  | Admin Interface Web Server |  | Restricted access to Administrators only.
| Local RFID Embedded System |  |  | Raspberry Pi Zero |  |  | SD Card failure
| Power |  |  | POE - Power Over Ethernet
| Programming Language |  |  | Python 3 or RUST
| Programming Style |  |  | State Machine design - no exception function with FAIL SAFE / FAIL SECURE.
| OS |  |  | Raspbian
| RFID Reader / Writers |  |  | RFID-RC522 panel | https://www.amazon.co.uk/IZOKEE-RFID-RC522-13-56MHz-Arduino-Raspberry/dp/B076HTH56Q/ref=sr_1_3?dchild=1&keywords=RFID-RC522&qid=1587974269&s=diy&sr=1-3 | .
| RFID Tags or Cards |  |  | 13.56 Mhz Cards or key ring tags
|  |  |  | Tags | https://www.amazon.co.uk/UHPPOTE-13-56MHz-Keyfob-Keytag-Keychain/dp/B00Y9FITPK/ref=sr_1_5?dchild=1&keywords=13.56mhz&qid=1587974178&sr=8-5 | .
|  |  |  | Cards | https://www.amazon.co.uk/YARONGTECH-13-56MHZ-MIFARE-Classic%C2%AE-control/dp/B01F52VQZ0/ref=sr_1_3?dchild=1&keywords=13.56mhz&qid=1587974178&sr=8-3 | .
| Feedback Screen |  |  | https://www.ebay.co.uk/itm/2-4-in-TFT-LCD-Display-Touch-Screen-Board-ILI9328-240x320-RGB-For-Raspberry-Pi/153833369993?hash=item23d12ef189:g:PDAAAOSwoCFd93QN
| Feedback Sounder |  |  | Cheapest internet option is £15. Consider small amplifiers using stock Ics and speaker.
https://www.ebay.co.uk/itm/DC5V-2W-Digital-Audio-Speaker-High-Power-Amp-Amplifier-Board-SC8002B-Chip/382707904052?_trkparms=aid%3D1110004%26algo%3DSPLICE.COMP%26ao%3D1%26asc%3D225076%26meid%3D03b4fb93bad24edca342d6a6228d569f%26pid%3D100008%26rk%3D5%26rkt%3D12%26sd%3D132631879720%26itm%3D382707904052%26pmt%3D1%26noa%3D0%26pg%3D2047675%26algv%3Ddefault%26brand%3DUnbranded&_trksid=p2047675.c100008.m2219
| Magnetic Door lock |  |  | https://www.ebay.co.uk/itm/373013765835
| Network |  |  | Ethernet CAT 5 Network, galvanically isolated from all other networks back to control server.
POE network switch?
| Lighting / Environmental control |  |  | Local GPIO / relay or power transistor control.
| Security |  |  | TAMPER sensory. Connection interruption, case opening switch.
| Break glass to exit |  |  | https://www.ebay.co.uk/itm/Emergency-Door-Release-Glass-Break-Alarm-Button-Fire-Alarm-Swtich-Break-I5Y8/164161727798?hash=item2638cd2d36:g:Bg0AAOSwXMZelo2T

## DoorAccess-Spec-SoftwareDesign
Concept Television Studios Limited
Building Management System - Door Access
SOFTWARE DESIGN
| 2020-04-27 | PME | Creation
Language Options
Python 3
Easy to write / read.
More mature libraries available - making functionality such as camera interaction and sound easier.
Less Secure
Code can be edited easily on the fly as it isn't compiled.
Long term failure
Memory leaks on loops and libraries are more apparent in previous projects.
RUST
More complicatd to create
Language is more fussy than Python, but will reduce chance of bugs in the long term
Timescales are one third longer for coding than Python
Fewer libraries with slower development available - making more advanced features such as camera, screen and sound more complicated.
MYSQL is however well supported.
More secure
Compiled language and CRC executable profile mitigates identified modified code running.
Less easy to directly hack due to compiled nature.
Less chance of long-term failure
Memory is tightly controlled. Loops correctly handled to avoid memory leaks resulting in progressive failure.
Architecture Risks and Technical Considerations
Raspberry Pi SD cards can corrupt.
Stock of spares or images required for quick repair.
Also higher quality Toshiba / Samsung brands, NOT cheap cards!
Malicious actor replaces SD Card with modified firmware
Unlikely as there would probably be easier ways to acquire assets or compromise access.
Revenue protection - regular external clients using paid services may try to compromise, but isolated CCTV system and TAMPER logs would mitigate.
Mitigate multiple ID scans - both multi-reads of same ID and the swift presentation of multiple IDs as more than one person access a space.
State Machine Process for local RFID embedded systems
Initialisation
State Machine Loop
Data PullPush
Read Access Requests
Exit Check
Exit
Function Descriptions
Initialisation
Load Libraries
Set variables
|  |  | Is Exit? | Determines environmental actions
Update Display with loading flash
Data PullPush
Pull FIRE Status
Act on Fire Status. (Only return to loop when fire status cleared)
Emergency EXIT Status
Act on Emergency EXIT Status (Only return to loop when status cleared)
Pull and set current Date and Time.
Pull temperature information (Studio, Hallway, Ext)
Pull current access list for specified location from Primary DB.
Push last access requests (and mark as pushed)
Read Access Requests
Query RFID for X TIME
IF - card presented, READ Card Data
Security Image Capture
IF - Check access list for permission
YES - Access Granted Location
NO - Access Denied Location
Access Granted Location
Action Environmental Control
Lights ON
Release Electro MAGNETIC Door Catch
Display "Access Granted - Name"
Log Access Request Accepted to LOCAL log.
IF door has been opened
READ door access sensor (alarm magetic) for door open.
Wait for X Time
Wait X time
Lock Electro MAGNETIC Door Catch
Still Image Capture
Access Denied Location
Display "Access Denied - Name. You are not permitted access to this room."
Log Access Request Denied to LOCAL log.
Lock Electro MAGNETIC Door Catch
Still Image Capture
Security Image Capture
Open CAMERA
Save STILL IMAGE to Local Location
Close CAMERA
Act on Fire Status.
Release Electro MAGNETIC Door Catch
Security Image Capture
Log Access Request FIRE to LOCAL log.
IF status = TRUE
WAIT x
Lock Electro MAGNETIC Door Catch
Emergency EXIT Status
Release Electro MAGNETIC Door Catch
Security Image Capture
Log Access Request Emergency EXIT to LOCAL log.
IF status = TRUE
WAIT x
Lock Electro MAGNETIC Door Catch
Release Electro MAGNETIC Door Catch
Set GPIO LOW
Lock Electro MAGNETIC Door Catch
Set GPIO HIGH
Log Access Request FIRE to LOCAL log.
RFID Detail